{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"images":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":58,"n_cols":13,"rows_kept":58,"merged":[[1,2,1,6],[1,8,1,12],[56,0,56,11],[57,0,57,11]],"flags":["formulas_cached_only"]}
[]
[null,null,"R-275**",{"$nulls":5},"415"]
["Line Pressure","Capacity Pressure Multiplier","Capacity scfh\n½\" wc diff \n0.6 SG Gas","Capacity scfh \n1\" wc diff* \n0.6 SG Gas","Maximum\nDial Rate (acfh)\n@ 1\" wc diff","Capacity scfh  \n2\" wc diff* \n0.6 SG Gas","Maximum\nDial Rate (acfh)\n@ 2\" wc diff",null,"Capacity scfh\n½\" wc diff \n0.6 SG Gas","Capacity scfh \n1\" wc diff* \n0.6 SG Gas","Maximum\nDial Rate (acfh)\n@ 1\" wc diff","Capacity scfh  \n2\" wc diff* \n0.6 SG Gas","Maximum\nDial Rate (acfh)\n@ 2\" wc diff"]
["7\" wc (.25 psig)",{"v":1,"d":"1.000"},275,410,410,600,600,null,415,620,620,900,900]
["8\" wc",{"v":1.0012115636031276,"d":"1.001"},{"v":275.33317999086006,"d":"275"},{"v":410.4967410772823,"d":"410"},{"v":409.50386002785,"d":"410"},{"v":600.7269381618765,"d":"601"},{"v":599.2739415041707,"d":"599"},null,{"v":415.50279889529793,"d":"416"},{"v":620.7511694339391,"d":"621"},{"v":619.2497395543098,"d":"619"},{"v":901.0904072428148,"d":"901"},{"v":898.910912256256,"d":"899"}]
["9\" wc",{"v":1.0024216628670986,"d":"1.002"},{"v":275.6659572884521,"d":"276"},{"v":410.9928817755104,"d":"411"},{"v":409.00951684077677,"d":"409"},{"v":601.4529977202591,"d":"601"},{"v":598.5505124499172,"d":"599"},null,{"v":416.0049900898459,"d":"416"},{"v":621.5014309776011,"d":"622"},{"v":618.5021961982478,"d":"619"},{"v":902.1794965803887,"d":"902"},{"v":897.8257686748758,"d":"898"}]
["10\" wc",{"v":1.0036303030886715,"d":"1.004"},{"v":275.99833334938467,"d":"276"},{"v":411.4884242663553,"d":"411"},{"v":408.51695961971785,"d":"409"},{"v":602.1781818532029,"d":"602"},{"v":597.8296970044652,"d":"598"},null,{"v":416.5065757817987,"d":"417"},{"v":622.2507879149763,"d":"622"},{"v":617.7573535712806,"d":"618"},{"v":903.2672727798043,"d":"903"},{"v":896.7445455066977,"d":"897"}]
["11\" wc",{"v":1.0048374895327492,"d":"1.005"},{"v":276.33030962150605,"d":"276"},{"v":411.9833707084272,"d":"412"},{"v":408.0261776365953,"d":"408"},{"v":602.9024937196496,"d":"603"},{"v":597.1114794681883,"d":"597"},null,{"v":417.0075581560909,"d":"417"},{"v":622.9992435103045,"d":"623"},{"v":617.0151954504612,"d":"617"},{"v":904.3537405794743,"d":"904"},{"v":895.6672192022825,"d":"896"}]
["12\" wc",{"v":1.0060432274326474,"d":"1.006"},{"v":276.661887543978,"d":"277"},{"v":412.4777232473854,"d":"412"},{"v":407.5371602533338,"d":"408"},{"v":603.6259364595884,"d":"604"},{"v":596.3958442731714,"d":"596"},null,{"v":417.50793938454865,"d":"418"},{"v":623.7468010082414,"d":"624"},{"v":616.2757057489438,"d":"616"},{"v":905.4389046893826,"d":"905"},{"v":894.5937664097571,"d":"895"}]
["13\" wc",{"v":1.0072475219903583,"d":"1.007"},{"v":276.9930685473485,"d":"277"},{"v":412.9714840160469,"d":"413"},{"v":407.04989692089276,"d":"407"},{"v":604.348513194215,"d":"604"},{"v":595.6827759817944,"d":"596"},null,{"v":418.00772162599867,"d":"418"},{"v":624.4934636340221,"d":"624"},{"v":615.5388685145208,"d":"616"},{"v":906.5227697913225,"d":"907"},{"v":893.5241639726916,"d":"894"}]
["14\" wc (.5 psig)",{"v":1.0084503783768128,"d":"1.008"},{"v":277.3238540536235,"d":"277"},{"v":413.4646551344933,"d":"413"},{"v":406.56437717831005,"d":"407"},{"v":605.0702270260877,"d":"605"},{"v":594.9722592853317,"d":"595"},null,{"v":418.50690702637735,"d":"419"},{"v":625.2392345936239,"d":"625"},{"v":614.8046679281761,"d":"615"},{"v":907.6053405391316,"d":"908"},{"v":892.4583889279976,"d":"892"}]
["15\" wc",{"v":1.0096518017321399,"d":"1.010"},{"v":277.6542454763385,"d":"278"},{"v":413.95723871017736,"d":"414"},{"v":406.080590651759,"d":"406"},{"v":605.7910810392839,"d":"606"},{"v":594.2642790025741,"d":"594"},null,{"v":419.00549771883806,"d":"419"},{"v":625.9841170739268,"d":"626"},{"v":614.07308830266,"d":"614"},{"v":908.6866215589258,"d":"909"},{"v":891.3964185038611,"d":"891"}]
["16\" wc",{"v":1.0108517971659228,"d":"1.011"},{"v":277.98424422062874,"d":"278"},{"v":414.44923683802836,"d":"414"},{"v":405.59852705361715,"d":"406"},{"v":606.5110782995537,"d":"607"},{"v":593.5588200784641,"d":"594"},null,{"v":419.503495823858,"d":"420"},{"v":626.7281142428722,"d":"627"},{"v":613.3441140810796,"d":"613"},{"v":909.7666174493305,"d":"910"},{"v":890.3382301176962,"d":"890"}]
["17\" wc",{"v":1.012050369757452,"d":"1.012"},{"v":278.31385168329933,"d":"278"},{"v":414.9406516005554,"d":"415"},{"v":405.1181761815477,"d":"405"},{"v":607.2302218544712,"d":"607"},{"v":592.8558675827527,"d":"593"},null,{"v":420.0009034493426,"d":"420"},{"v":627.4712292496203,"d":"627"},{"v":612.6177298355111,"d":"613"},{"v":910.8453327817069,"d":"911"},{"v":889.2838013741291,"d":"889"}]
["18\" wc",{"v":1.0132475245559769,"d":"1.013"},{"v":278.64306925289367,"d":"279"},{"v":415.4314850679505,"d":"415"},{"v":404.6395279175928,"d":"405"},{"v":607.9485147335861,"d":"608"},{"v":592.1554067086723,"d":"592"},null,{"v":420.4977226907304,"d":"420"},{"v":628.2134652247057,"d":"628"},{"v":611.8939202656281,"d":"612"},{"v":911.9227721003792,"d":"912"},{"v":888.2331100630086,"d":"888"}]
["19\" wc",{"v":1.014443266580953,"d":"1.014"},{"v":278.9718983097621,"d":"279"},{"v":415.92173929819074,"d":"416"},{"v":404.16257222727774,"d":"404"},{"v":608.6659599485719,"d":"609"},{"v":591.4574227716259,"d":"591"},null,{"v":420.9939556310955,"d":"421"},{"v":628.9548252801909,"d":"629"},{"v":611.1726701973467,"d":"611"},{"v":912.9989399228577,"d":"913"},{"v":887.1861341574389,"d":"887"}]
["20\" wc",{"v":1.0156376008222883,"d":"1.016"},{"v":279.30034022612926,"d":"279"},{"v":416.4114163371382,"d":"416"},{"v":403.68729915872814,"d":"404"},{"v":609.3825604933729,"d":"609"},{"v":590.7619012078948,"d":"591"},null,{"v":421.4896043412496,"d":"421"},{"v":629.6953125098187,"d":"630"},{"v":610.4539645814913,"d":"610"},{"v":914.0738407400595,"d":"914"},{"v":886.1428518118423,"d":"886"}]
["21\" wc (.75 psig)",{"v":1.016830532240586,"d":"1.017"},{"v":279.62839636616116,"d":"280"},{"v":416.90051821864023,"d":"417"},{"v":403.21369884179717,"d":"403"},{"v":610.0983193443516,"d":"610"},{"v":590.0688275733618,"d":"590"},null,{"v":421.9846708798432,"d":"422"},{"v":630.4349299891633,"d":"630"},{"v":609.7377884924738,"d":"610"},{"v":915.1474790165273,"d":"915"},{"v":885.1032413600426,"d":"885"}]
["22\" wc",{"v":1.0180220657673846,"d":"1.018"},{"v":279.95606808603077,"d":"280"},{"v":417.3890469646277,"d":"417"},{"v":402.7417614872052,"d":"403"},{"v":610.8132394604307,"d":"611"},{"v":589.3781875422516,"d":"589"},null,{"v":422.4791572934646,"d":"422"},{"v":631.1736807757785,"d":"631"},{"v":609.0241271269933,"d":"609"},{"v":916.2198591906462,"d":"916"},{"v":884.0672813133773,"d":"884"}]
["23\" wc",{"v":1.0192122063053957,"d":"1.019"},{"v":280.2833567339838,"d":"280"},{"v":417.8770045852122,"d":"418"},{"v":402.2714773856898,"d":"402"},{"v":611.5273237832374,"d":"612"},{"v":588.6899669058876,"d":"589"},null,{"v":422.9730656167392,"d":"423"},{"v":631.9115679093453,"d":"632"},{"v":608.3129658027505,"d":"608"},{"v":917.2909856748561,"d":"917"},{"v":883.0349503588313,"d":"883"}]
["24\" wc",{"v":1.0204009587287401,"d":"1.020"},{"v":280.61026365040357,"d":"281"},{"v":418.36439307878345,"d":"418"},{"v":401.8028369071662,"d":"402"},{"v":612.2405752372441,"d":"612"},{"v":588.0041515714628,"d":"588"},null,{"v":423.46639787242714,"d":"423"},{"v":632.6485944118189,"d":"633"},{"v":607.6042899571781,"d":"608"},{"v":918.3608628558661,"d":"918"},{"v":882.0062273571941,"d":"882"}]
["25\" wc",{"v":1.0215883278831799,"d":"1.022"},{"v":280.93679016787445,"d":"281"},{"v":418.85121443210375,"d":"419"},{"v":401.3358304998999,"d":"401"},{"v":612.9529967299079,"d":"613"},{"v":587.320727560829,"d":"587"},null,{"v":423.95915607151966,"d":"424"},{"v":633.3847632875716,"d":"633"},{"v":606.89808514619,"d":"607"},{"v":919.4294950948619,"d":"919"},{"v":880.9810913412437,"d":"881"}]
["26\" wc",{"v":1.0227743185863494,"d":"1.023"},{"v":281.26293761124606,"d":"281"},{"v":419.3374706204032,"d":"419"},{"v":400.8704486896882,"d":"401"},{"v":613.6645911518096,"d":"614"},{"v":586.6396810092999,"d":"587"},null,{"v":424.451342213335,"d":"424"},{"v":634.1200775235366,"d":"634"},{"v":606.1943370429432,"d":"606"},{"v":920.4968867277145,"d":"920"},{"v":879.9595215139499,"d":"880"}]
["27\" wc",{"v":1.0239589356279823,"d":"1.024"},{"v":281.5887072976951,"d":"282"},{"v":419.82316360747274,"d":"420"},{"v":400.4066820790539,"d":"400"},{"v":614.3753613767894,"d":"614"},{"v":585.9609981644692,"d":"586"},null,{"v":424.9429582856127,"d":"425"},{"v":634.854540089349,"d":"635"},{"v":605.4930314366181,"d":"605"},{"v":921.5630420651842,"d":"922"},{"v":878.9414972467038,"d":"879"}]
["28\" wc (1 psig)",{"v":1.0251421837701393,"d":"1.025"},{"v":281.91410053678834,"d":"282"},{"v":420.30829534575713,"d":"420"},{"v":399.9445213464472,"d":"400"},{"v":615.0853102620836,"d":"615"},{"v":585.2846653850446,"d":"585"},null,{"v":425.43400626460783,"d":"425"},{"v":635.5881539374864,"d":"636"},{"v":604.7941542312128,"d":"605"},{"v":922.6279653931254,"d":"923"},{"v":877.926998077567,"d":"878"}]
["1.25 psig",{"v":1.0333869858834814,"d":"1.033"},{"v":284.18142111795737,"d":"284"},{"v":423.68866421222737,"d":"424"},{"v":396.7535933786466,"d":"397"},{"v":620.0321915300889,"d":"620"},{"v":580.6150147004585,"d":"581"},null,{"v":428.8555991416448,"d":"429"},{"v":640.6999312477585,"d":"641"},{"v":599.9688485238071,"d":"600"},{"v":930.0482872951333,"d":"930"},{"v":870.9225220506877,"d":"871"}]
["1.5 psig",{"v":1.0415665260758353,"d":"1.042"},{"v":286.4307946708547,"d":"286"},{"v":427.04227569109247,"d":"427"},{"v":393.63784236106324,"d":"394"},{"v":624.9399156455012,"d":"625"},{"v":576.0553790649707,"d":"576"},null,{"v":432.25010832147166,"d":"432"},{"v":645.7712461670179,"d":"646"},{"v":595.257225033803,"d":"595"},{"v":937.4098734682518,"d":"937"},{"v":864.083068597456,"d":"864"}]
["1.75 psig",{"v":1.0496823299884688,"d":"1.050"},{"v":288.6626407468289,"d":"289"},{"v":430.36975529527217,"d":"430"},{"v":390.59436201474784,"d":"391"},{"v":629.8093979930812,"d":"630"},{"v":571.6015053874359,"d":"572"},null,{"v":435.61816694521457,"d":"436"},{"v":650.8030445928506,"d":"651"},{"v":590.6548889003504,"d":"591"},{"v":944.7140969896219,"d":"945"},{"v":857.4022580811538,"d":"857"}]
["2 psig",{"v":1.057735864731057,"d":"1.058"},{"v":290.8773628010407,"d":"291"},{"v":433.6717045397334,"d":"434"},{"v":387.62040096300206,"d":"388"},{"v":634.6415188386343,"d":"635"},{"v":567.2493672629298,"d":"567"},null,{"v":438.9603838633887,"d":"439"},{"v":655.7962361332554,"d":"656"},{"v":586.1576795050275,"d":"586"},{"v":951.9622782579513,"d":"952"},{"v":850.8740508943946,"d":"851"}]
["2.25 psig",{"v":1.0657285419780658,"d":"1.066"},{"v":293.07534904396806,"d":"293"},{"v":436.94870221100695,"d":"437"},{"v":384.71335227544125,"d":"385"},{"v":639.4371251868395,"d":"639"},{"v":562.9951496713775,"d":"563"},null,{"v":442.2773449208973,"d":"442"},{"v":660.7516960264007,"d":"661"},{"v":581.7616546604233,"d":"582"},{"v":959.1556877802592,"d":"959"},{"v":844.4927245070662,"d":"844"}]
["2.5 psig",{"v":1.0736617208576595,"d":"1.074"},{"v":295.2569732358564,"d":"295"},{"v":440.2013055516404,"d":"440"},{"v":381.8707438619353,"d":"382"},{"v":644.1970325145958,"d":"644"},{"v":558.8352349199054,"d":"559"},null,{"v":445.5696141559287,"d":"446"},{"v":665.6702669317489,"d":"666"},{"v":577.4630760839021,"d":"577"},{"v":966.2955487718936,"d":"966"},{"v":838.2528523798579,"d":"838"}]
["2.75 psig",{"v":1.0815367106498823,"d":"1.082"},{"v":297.4225954287176,"d":"297"},{"v":443.4300513664518,"d":"443"},{"v":379.0902296359742,"d":"379"},{"v":648.9220263899294,"d":"649"},{"v":554.7661897111817,"d":"555"},null,{"v":448.8377349197012,"d":"449"},{"v":670.552760602927,"d":"671"},{"v":573.2583960348877,"d":"573"},{"v":973.383039584894,"d":"973"},{"v":832.1492845667725,"d":"832"}]
["3 psig",{"v":1.0893547733092759,"d":"1.089"},{"v":299.5725626600509,"d":"300"},{"v":446.6354570568031,"d":"447"},{"v":376.36958137566995,"d":"376"},{"v":653.6128639855656,"d":"654"},{"v":550.7847532326878,"d":"551"},null,{"v":452.08223092334947,"d":"452"},{"v":675.3999594517511,"d":"675"},{"v":569.1442450071107,"d":"569"},{"v":980.4192959783483,"d":"980"},{"v":826.1771298490315,"d":"826"}]
["3.25 psig",{"v":1.097117125825698,"d":"1.097"},{"v":301.70720960206694,"d":"302"},{"v":449.81802158853617,"d":"450"},{"v":373.7066812182256,"d":"374"},{"v":658.2702754954188,"d":"658"},{"v":546.8878261730131,"d":"547"},null,{"v":455.30360721766465,"d":"455"},{"v":680.2126180119327,"d":"680"},{"v":565.1174203787801,"d":"565"},{"v":987.4054132431282,"d":"987"},{"v":820.3317392595196,"d":"820"}]
["3.5 psig",{"v":1.1048249424358492,"d":"1.105"},{"v":303.8268591698585,"d":"304"},{"v":452.97822639869815,"d":"453"},{"v":371.0995147304129,"d":"371"},{"v":662.8949654615095,"d":"663"},{"v":543.0724605810921,"d":"543"},null,{"v":458.5023511108774,"d":"459"},{"v":684.9914643102264,"d":"685"},{"v":561.1748759337951,"d":"561"},{"v":994.3424481922642,"d":"994"},{"v":814.608690871638,"d":"815"}]
["3.75 psig",{"v":1.1124793566968847,"d":"1.112"},{"v":305.9318230916433,"d":"306"},{"v":456.1165362457227,"d":"456"},{"v":368.5461645035378,"d":"369"},{"v":667.4876140181308,"d":"667"},{"v":539.3358504929821,"d":"539"},null,{"v":461.67893302920714,"d":"462"},{"v":689.7372011520686,"d":"690"},{"v":557.3137121760816,"d":"557"},{"v":1001.2314210271962,"d":"1001"},{"v":809.0037757394732,"d":"809"}]
["4 psig",{"v":1.120081463432482,"d":"1.120"},{"v":308.02240244393255,"d":"308"},{"v":459.23340000731764,"d":"459"},{"v":366.04480422661203,"d":"366"},{"v":672.0488780594892,"d":"672"},{"v":535.6753232584566,"d":"536"},null,{"v":464.83380732448006,"d":"465"},{"v":694.4505073281389,"d":"694"},{"v":553.5311673670718,"d":"554"},{"v":1008.0733170892338,"d":"1008"},{"v":803.5129848876849,"d":"804"}]
["4.25 psig",{"v":1.1276323205608234,"d":"1.128"},{"v":310.0988881542264,"d":"310"},{"v":462.3292514299376,"d":"462"},{"v":363.59369319610147,"d":"364"},{"v":676.579392336494,"d":"677"},{"v":532.08833150649,"d":"532"},null,{"v":467.9674130327417,"d":"468"},{"v":699.1320387477106,"d":"699"},{"v":549.824609223373,"d":"550"},{"v":1014.8690885047411,"d":"1015"},{"v":798.1324972597349,"d":"798"}]
["4.5 psig",{"v":1.1351329508131303,"d":"1.135"},{"v":312.16156147361085,"d":"312"},{"v":465.40450983338343,"d":"465"},{"v":361.1911712247491,"d":"361"},{"v":681.0797704878781,"d":"681"},{"v":528.5724456947547,"d":"529"},null,{"v":471.08017458744905,"d":"471"},{"v":703.7824295041407,"d":"704"},{"v":546.1915272179132,"d":"546"},{"v":1021.6196557318173,"d":"1022"},{"v":792.8586685421321,"d":"793"}]
["4.75 psig",{"v":1.142584343350661,"d":"1.143"},{"v":314.2106944214318,"d":"314"},{"v":468.45958077377105,"d":"468"},{"v":358.8356539156342,"d":"359"},{"v":685.5506060103967,"d":"686"},{"v":525.1253471936111,"d":"525"},null,{"v":474.1725024905243,"d":"474"},{"v":708.4022928774099,"d":"708"},{"v":542.6295254333982,"d":"543"},{"v":1028.325909015595,"d":"1028"},{"v":787.6880207904167,"d":"788"}]
["5 psig",{"v":1.1499874552874034,"d":"1.150"},{"v":316.24655020403594,"d":"316"},{"v":471.4948566678354,"d":"471"},{"v":356.52562827090435,"d":"357"},{"v":689.992473172442,"d":"690"},{"v":521.7448218598599,"d":"522"},null,{"v":477.24479394427243,"d":"477"},{"v":712.9922222781901,"d":"713"},{"v":539.1363159218553,"d":"539"},{"v":1034.9887097586632,"d":"1035"},{"v":782.61723278979,"d":"783"}]
["6 psig",{"v":1.1791351957734721,"d":"1.179"},{"v":324.2621788377048,"d":"324"},{"v":483.4454302671236,"d":"483"},{"v":347.71246034349275,"d":"348"},{"v":707.4811174640832,"d":"707"},{"v":508.8475029416967,"d":"509"},null,{"v":489.34110624599094,"d":"489"},{"v":731.0638213795527,"d":"731"},{"v":525.8090863730865,"d":"526"},{"v":1061.221676196125,"d":"1061"},{"v":763.2712544125451,"d":"763"}]
["7 psig",{"v":1.2075795926170216,"d":"1.208"},{"v":332.08438796968096,"d":"332"},{"v":495.1076329729789,"d":"495"},{"v":339.5221337845427,"d":"340"},{"v":724.547755570213,"d":"725"},{"v":496.86165919689176,"d":"497"},null,{"v":501.145530936064,"d":"501"},{"v":748.6993474225534,"d":"749"},{"v":513.4237145034548,"d":"513"},{"v":1086.8216333553194,"d":"1087"},{"v":745.2924887953376,"d":"745"}]
["8 psig",{"v":1.235369230270221,"d":"1.235"},{"v":339.7265383243108,"d":"340"},{"v":506.50138441079065,"d":"507"},{"v":331.8845815111631,"d":"332"},{"v":741.2215381621327,"d":"741"},{"v":485.6847534309704,"d":"486"},null,{"v":512.6782305621417,"d":"513"},{"v":765.9289227675371,"d":"766"},{"v":501.87424521200273,"d":"502"},{"v":1111.832307243199,"d":"1112"},{"v":728.5271301464556,"d":"729"}]
["9 psig",{"v":1.2625473447327769,"d":"1.263"},{"v":347.2005198015136,"d":"347"},{"v":517.6444113404385,"d":"518"},{"v":324.7402972335886,"d":"325"},{"v":757.5284068396661,"d":"758"},{"v":475.22970326866624,"d":"475"},null,{"v":523.9571480641024,"d":"524"},{"v":782.7793537343216,"d":"783"},{"v":491.07069337762175,"d":"491"},{"v":1136.2926102594993,"d":"1136"},{"v":712.8445549029994,"d":"713"}]
["10 psig",{"v":1.289152613263896,"d":"1.289"},{"v":354.5169686475714,"d":"355"},{"v":528.5525714381973,"d":"529"},{"v":318.0383732550918,"d":"318"},{"v":773.4915679583376,"d":"773"},{"v":465.4220096415978,"d":"465"},null,{"v":534.9983345045168,"d":"535"},{"v":799.2746202236154,"d":"799"},{"v":480.93607662965104,"d":"481"},{"v":1160.2373519375064,"d":"1160"},{"v":698.1330144623968,"d":"698"}]
["11 psig",{"v":1.3152198002153401,"d":"1.315"},{"$nulls":6},{"v":545.8162170893662,"d":"546"},{"v":815.4362761335109,"d":"815"},{"v":471.40409526870553,"d":"471"},{"v":1183.6978201938061,"d":"1184"},{"v":684.2962673255403,"d":"684"}]
["12 psig",{"v":1.3407802897834626,"d":"1.341"},{"$nulls":6},{"v":556.423820260137,"d":"556"},{"v":831.2837796657468,"d":"831"},{"v":462.4172988850624,"d":"462"},{"v":1206.7022608051163,"d":"1207"},{"v":671.2509177363809,"d":"671"}]
["13 psig",{"v":1.365862528977632,"d":"1.366"},{"$nulls":6},{"v":566.8329495257173,"d":"567"},{"v":846.8347679661318,"d":"847"},{"v":453.92562344036116,"d":"454"},{"v":1229.276276079869,"d":"1229"},{"v":658.9242920908468,"d":"659"}]
["14 psig",{"v":1.3904923986338509,"d":"1.390"},{"$nulls":6},{"v":577.0543454330481,"d":"577"},{"v":862.1052871529876,"d":"862"},{"v":445.88521347484226,"d":"446"},{"v":1251.4431587704657,"d":"1251"},{"v":647.2527292376742,"d":"647"}]
["15 psig",{"v":1.4146935262635039,"d":"1.415"},{"$nulls":6},{"v":587.0978133993541,"d":"587"},{"v":877.1099862833725,"d":"877"},{"v":438.257466009297,"d":"438"},{"v":1273.2241736371534,"d":"1273"},{"v":636.1801925941407,"d":"636"}]
["20 psig",{"v":1.5299676748933624,"d":"1.530"},{"$nulls":6},{"v":634.9365850807454,"d":"635"},{"v":948.5799584338847,"d":"949"},{"v":405.23731982978893,"d":"405"},{"v":1376.970907404026,"d":"1377"},{"v":588.2477223335645,"d":"588"}]
["25 psig",{"v":1.6371451979544565,"d":"1.637"},{"$nulls":6},{"v":679.4152571510995,"d":"679"},{"v":1015.030022731763,"d":"1015"},{"v":378.7080100009845,"d":"379"},{"v":1473.4306781590108,"d":"1473"},{"v":549.7374338723968,"d":"550"}]
[]
["R-275 Standard MAOP Pressure - 5 psig, 10 psig Optional; 415 Standard MAOP - 10 psig, 25 psig Optional"]
["The numbers in the chart below are calculated and may vary from the published values which are based on performance testing."]
["Base pressure 14.73 psia, Base temperature 60°F, 0.6 SG Natural Gas, Capacities stated in standard cubic feet unless otherwise noted."]
["** Data is provided for reference only at the request of the customer and does not imply any type of warranty or recommendations of use."]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}